## Slide 1
SMART CAMPUS ENERGY
Fuzzy-GA Hybrid
Optimization
Trading modeled energy use against occupant comfort, zone by zone
A reproducible local simulation prototype
Faculty presentation · 9 October 2026
Notes: Based on the supplied paper, “A Fuzzy-GA Hybrid Framework for Smart Campus Energy Consumption Optimization Under Occupant Comfort Constraints.” The included demo is an independent educational implementation and does not reproduce the paper’s experiment.

## Slide 2
PROBLEM
The control problem is a trade-off
Fuzzy-GA Smart Campus Energy Optimization
A fixed schedule applies the same policy across rooms whose use changes through the day.
EMPTY ROOM
Unnecessary cooling and lighting add avoidable load.
BUSY ROOM
Relaxed setpoints can increase discomfort when occupancy is high.
DESIGN GOAL
Reduce modeled energy while keeping comfort risk visible in the objective.
Optimization target
Zone-specific setpoint + ventilation + lighting
Notes: The source paper motivates the task using occupancy variation and thermal comfort. Its annual trace is synthetic; this slide describes the optimization problem, not measured campus outcomes.

## Slide 3
METHOD
Fuzzy reasoning guides the genetic search
Fuzzy-GA Smart Campus Energy Optimization
Each chromosome is scored using energy and comfort information computed from that candidate.
Scenario inputs
12 zones
occupancy · weather
room state
Mamdani-style FIS
27 max-min rules
inputs include candidate
CO₂ and setpoint offset
Fitness evaluation
energy proxy + CRI
PMV comfort penalty
penalty grows by generation
Real-coded GA
selection · crossover
mutation · elitism
36 decision values
→
→
→
Selected schedule preview
The browser dashboard displays the optimized settings and convergence trace; no control signal is sent to equipment.
Notes: Source: supplied Fuzzy-GA paper, Sections IV–V. The prototype uses a compact 27-rule implementation, a one-hour scenario, and an educational energy proxy.

## Slide 4
MODEL
A 36-value chromosome represents 12 zones
Fuzzy-GA Smart Campus Energy Optimization
For each zone z
[ Tz, Vz, Lz ]
Setpoint 22–27 °C Ventilation 0.3–1.0 Lighting 0.2–1.0
CANDIDATE →
Estimate energy and CO₂
→
Infer comfort risk
→
Score and evolve
Fitness = (1 − w) × normalized energy + w × mean CRI + λ × CRI-weighted PMV excess
The comfort weight exposes the energy–comfort preference; λ increases as generations advance.
Notes: The chromosome bounds, comfort terms, Mamdani-style inference and real-coded GA follow the supplied paper’s structure. This prototype uses a compact approximation; the objective and coefficients are not a calibrated building model.

## Slide 5
RESULTS
Two result sets; two different experiments
Fuzzy-GA Smart Campus Energy Optimization
LOCAL DEMO · ONE SYNTHETIC HOUR
86.8
→
59.1
modeled kWh proxy · fixed schedule
modeled kWh proxy · GA candidate
31.8% lower modeled energy
Mean |PMV|: 0.16 → 0.37 · PMV > 0.5: 0% → 8.3%
PAPER-REPORTED · SYNTHETIC YEAR TRACE
21.4%
reported daily energy reduction for the paper’s separate 8,760-hour synthetic trace
These figures are not directly comparable.
The demo uses a different scenario, model, horizon and evaluation protocol.
All local-demo values are model outputs, not measured campus savings.
Notes: The source paper reports 21.4% savings in its own one-year synthetic academic-block trace. Local prototype result: fixed seed 7, comfort weight 0.4, 12 synthetic zones, one-hour energy proxy. Baseline 86.751 proxy kWh; optimized 59.144 proxy kWh; modeled mean absolute PMV 0.158 to 0.375; threshold violation rate 0% to 8.3%. The scenarios and evaluation methods differ, so the percentages must not be compared as equivalent evidence.

## Slide 6
SCOPE
What is built and what still needs validation
Fuzzy-GA Smart Campus Energy Optimization
BUILT FOR THE DEMONSTRATION
• Local browser dashboard
• 12-zone, 36-decision GA search
• Interpretable fuzzy-rule score
• PMV, CRI, energy and convergence views
NEXT RESEARCH STEPS
1. Calibrate with measured campus telemetry
2. Validate comfort rules against occupant feedback
3. Compare baselines under equal evaluation budgets
4. Test in shadow mode before any control deployment
Current limitations
Synthetic inputs · one-hour horizon · approximate energy model · fixed PMV assumptions
Questions
Notes: The supplied paper itself lists model simplification, fixed PMV assumptions, synthetic energy data and lack of real occupant surveys as validity threats. This prototype is for demonstration and education, not operational dispatch.